## Design List
Design List - Hydropower Design Procedure |  | Stream sro
| The procedure presents the typical breakdown of the hydro power project. Usually some pieces of information are available sooner or later, the procedure thus will be adopted to the each project according to the data availability and other aspects. | 2019-03-24 11:00
Based on initial consultation or initial information the selection of specific parts can be offered by our side and approved / completed by Client.
| Design | Selection
1 | Preliminary Data - Desk Study | please select
The preliminary data are available from the maps, web sites, information obtained from authorities etc. The data are completed before the site visit, the necessary surveys for data extension are specified based on the Preliminary Data and site visit. The result of the preliminary data evaluation is Desk Study (Estimation Report), which is simply based on data available at the preliminary stage. The data consists mainly of the following:
1.1 | Precipitation measurement on the river catchment area and nearby (long-term period, the longer the better)
1.2 | Flow measurement on the river section of the intake or nearby or on the near river (long-term period, the longer the better, usually the water level is monitored in daily step and the river flow is calculated from the equation based on measured flow at known water depth)
1.3 | Elevation contour map
1.4 | Geologic and seismic map - this information is usually requested in geologic survey specification, but if some data are available in advance it is used in Site Inspection Report
1.5 | Power connection point - place of connection, voltage, connection conditions (generators cos Fi, metering cube details etc.), possible power line route
1.6 | List of land owners of the supposed affected property, map of land owners
1.7 | Other social, environmental or politic aspects related to the project (e.g. Obligatory of employment, protection area, etc.)
1.8 | General information related to the hydro power (each country has specific laws or other demands related to hydro power projects)
1.9 | Desk study
The desk study main results:
• Location potential (theoretical annual power generation, achievable power, rated head and rated discharge)
• Outline design - basic layout (including more options if they exist)
2 | Site Inspection - Site Inspection Report | please select
2.1 | Site inspection is executed based on Desk Study. Except the supposed power plant objects there are also visited measurement stations (measurement verification could be realized) of the used data and important places related to the project. The main result of the site inspection is: | … ...
2.2 | Site Inspection Report | … ...
The report main result are following:
• Approval, extension or correction of Desk Study
• Surveys specification
Following the Site Inspection Report the surveys are performed in order to complete the supporting data for the next documentation level, the main surveys are usually:
2.3 | Geologic survey | … ...
2.4 | Topographic measurement | … ...
2.5 | Hydrologic survey | … ...
2.6 | Other survey - please specify… | … ...
2.7 | Power grid connection request (in order to receive connection point information) | … ...
3 | Feasibility Study | please select
3.1 | Feasibility Study
The main result is one scheme of one or more options based on the complete supporting data (surveys). The main parts are following:
| • Rated parameters (head, flow, residual flow, head water level, water abstraction place, powerhouse outlet connection place) | … ...
| • Conceptual layouts, sections, technology proposal, connection roads, connecting powerlines, temporary structures, basic hydraulic calculation | … ...
| • Economic evaluation (project cost, power generation, project income, financial model) | … ...
| • Risks and uncertainties | … ...
3.2 | Option determination (based on the results the consultant recommends and the client determines the option for the next documentation level)
The chosen option main parameters are submitted in order to receive licenses:
3.3 | Power connection license (connection point, voltage and other conditions) | … ...
3.4 | Water license (water abstraction place, max. rated flow, residual flow, power plant outlet place, other conditions) | … ...
3.5 | Land rights contracting (rented or purchased) | … ...
3.6 | Environmental license | … ...
4 | Basic Design | please select
4.1 | Basic Design
The basic design extends the previous design. The basic design is focused on the structures shapes and dimensions to be in accordance with the operation requirements, it doesn´t include structural and static details. Generally it is used for building permit and project tendering. The technology is included as final solution on level applicable for manufacturers tendering and contracting. It will consists of the following parts:
4.1.1 | General part | … ...
• General report (concluding site conditions, background papers and surveys information, circumstances, Client conditions and project main parameters & features)
• General layout (including objects numbering & subdivision)
• Construction procedure (project procedure timetable)
4.1.2 | Civil part | … ...
| • Layouts (including infrastructure connection (roads, bridges, power line, water ducts, others…) | … ...
| • Setting-out plans | … ...
| • Foundation pits design, ground water solution, phases of construction procedure, temporary structures | … ...
| • Hydraulic calculation (whole water way (hydrostatic & hydro dynamic analysis (water hammer)), auxiliary spillways, pipes, flushing's, operation water levels (OWL), flood water levels (FWL)), Q-H characteristics of power plant | … ...
| • Structural basic layouts and sections, including technology installation | … ...
| • Basic static calculation (stability and important calculation) | … ...
| • Architectural views or visualization of objects implementation in landscape | … ...
| • Typical cross sections of linear constructions (underground cables, pipes, roads etc.) | … ...
| • Pipes and penstocks design (layout, longitudinal sections, typical cross sections, fittings) | … ...
| • Bill of quantities (BoQ) | … ...
| • Other specific designs (air condition, noise impact...) | … ...
| Please specify… | … ...
4.1.3 | Mechanical Part
| • Technology basic description (technologic component disposal, basic parameters, materials, painting system, basic load & capacity ) (main technology (turbines, generators) & auxiliary hydrotechnical equipment (gates, cleaning machine…) | … ...
• Technology detail description - List of signals, scheme of automatics
| • Technology operation description & maintenance plan | … ...
| • Auxiliary piping - schemes, routes and specification (optionally implemented in civil design), (cooling, greasing…) | … ...
| • BoQ | … ...
4.1.4 | Electric Part
| • Electric part conception (single line diagram, disposal of substations and main electric equipment) | … ...
| • High voltage - basic parameters of main electric equipment (main transformer, station service transformer, switchboards, cable ducts…) | … ...
| • Low voltage - AC/DC distribution, control and protection system description | … ...
| • Single line diagrams of all switchboards & substations | … ...
| • Power line connection | … ...
| • Communication scheme | … ...
| • Lighting and small power installation | … ...
| • Miscellaneous (fire alarm & protection system, earthing...) | … ...
| Please specify… | … ...
| • BoQ | … ...
4.1.5 | Economic Part
| • Economic report (CAPEX, OPEX, annual power generation, financial model, basic economic parameters (NPV, IRR, DSCR)) | … ...
| • Risks & uncertainties report (SWOT analysis...) | … ...
4.2 | Basic Design Approval (client approves the proposed design level)
4.3 | Building permit procedure (basic design is usually used for building permit)
5 | Detailed Design
Detailed design extends the basic design into execution level, the main activity are following:
| • Setting out plans | … ...
| • Detailed static calculation | … ...
| • Reinforcement drawings | … ...
| • Structural details drawings | … ...
| • Construction self-frequency analysis | … ...
| • Metal works | … ...
| • Locksmith works | … ...
| • Auxiliary cables & piping tracks | … ...
| • Bill of quantities (civil part) | … ...
| • Civil electric installation & lighting design | … ...
| • Earthing | … ...
| • Mechanical equipment structural structural anchoring | … ...
| • Electric equipment detailed design | … ...
Other specific designs (security and fire protection, ventilation…) on require
| … specify… | … ...
| … specify… | … ...
Note: Detailed mechanical equipment information from the manufacturer is necessary for detailed design